## Español
Cálculo de ablandador Aquathin | [6 empty] | 65 |  | 1m3 = | 35.31 cft
|  |  | 30 | días / mes |  | granos req./ día: | 2891997.7865 |  | 1cft = | 28.32 litro
caudal día | 312 | m3/día | 82421.9369 | gpd |  | unidades | 2 |  | 1gal. = | 3.79 litro
caudal punta | 21 | m3/h | 92.4605 | gpm |  | caudal punta | 350 | l/min. | 1m3 = | 264.17 gal.
dureza | 600 | ppm | 35.0877 | granos |  | velocidad punta | 1.7597 | m/s | 1grano = | 17.1 ppm
Fe + Mn | 0 | ppm | 0 | granos |  | Ø de tubería: | 2 1/2 | " | 1psi = | 0.71mwc
cantidad de
| pie 3 res. | capacidad | regen. por | caudal | regen./ | kg. de sal | max. caudal pta. |  | % creci- | total de granos | gal. prog.
Unit model: | por cilind. | gran./ cilind. | día / cilind. | punta gpm | día/cilind. | req. / mes | posible gpm | uso | miento | sistema / día | válvula
HFD-SYN150K | 5 | 150000 | 6 | 48 | 5.133 | 12572.988 | 96 | OK | 24.48% | 3600000 | 4014.2857
HFD-SYN240K | 8 | 240000 | 6 | 48 | 3.1911 | 12506.2288 | 96 | OK | 99.17% | 5760000 | 6457.1429
HFD-SYN300K | 10 | 300000 | 6 | 48 | 2.5484 | 12484.133 | 96 | OK | 149% | 7200000 | 8085.7143
SYN 25K | 0.83333 | 25000 | 6 | 24 | 34.7372 | 14181.0275 | 48 | No | -79.25% | 600000 | 593.1818
SYN 30K | 1 | 30000 | 6 | 24 | 28.5107 | 13966.9743 | 48 | No | -75.1% | 720000 | 722.7273
SYN 45K | 1.5 | 45000 | 6 | 24 | 18.5407 | 13624.2265 | 48 | No | -62.66% | 1080000 | 1111.3636
SYN 75K | 2.5 | 75000 | 6 | 24 | 10.9102 | 13361.9068 | 48 | No | -37.76% | 1800000 | 1888.6364
ASC 15K/F | 0.5 | 15000 | 1 | 17 | 96.3999 | 52646.0781 | 34 | No | -98.96% | 30000 | 319.5652
ASC 25K/F | 0.83333 | 25000 | 1 | 17 | 57.84 | 49418.7323 | 34 | No | -98.27% | 50000 | 567.3913
ASC 40K/F | 1.3333 | 40000 | 1 | 17 | 36.15 | 47771.4413 | 34 | No | -97.23% | 80000 | 939.1304
ASC 45K/F | 1.5 | 45000 | 1 | 17 | 32.1333 | 47478.3649 | 34 | No | -96.89% | 90000 | 1063.0435
ASC 60K/F | 2 | 60000 | 1 | 17 | 24.1 | 46902.8696 | 34 | No | -95.85% | 120000 | 1434.7826
Mini Sodialite2k | 0.053333 | 1600 | 1 | 5 | 0.0011065 | días | 10 | No | -99.89% | 3200
AS2850-150K | 5 | 150000 | 1 | 48 | 9.64 | 45901.3848 | 96 | No | -89.63% | 300000 | 3665.2174
AS2850-240K | 8 | 240000 | 1 | 48 | 6.025 | 45657.6607 | 96 | No | -83.4% | 480000 | 5895.6522
AS2850-300K | 10 | 300000 | 1 | 48 | 4.82 | 45576.9934 | 96 | No | -79.25% | 600000 | 7382.6087
AS2900-240K | 8 | 240000 | 1 | 84 | 6.025 | 45657.6607 | 168 | No | -83.4% | 480000 | 5895.6522
AS2900-300K | 10 | 300000 | 1 | 84 | 4.82 | 45576.9934 | 168 | No | -79.25% | 600000 | 7382.6087
AS2900-510K | 17 | 510000 | 1 | 84 | 2.8353 | 45444.7493 | 168 | No | -64.73% | 1020000 | 12586.9565
AS3900-300K | 10 | 300000 | 1 | 105 | 4.82 | 45576.9934 | 210 | No | -79.25% | 600000 | 7382.6087
AS3900-510K | 17 | 510000 | 1 | 105 | 2.8353 | 45444.7493 | 210 | No | -64.73% | 1020000 | 12586.9565
AS3900-750K | 25 | 750000 | 1 | 105 | 1.928 | 45384.5501 | 210 | No | -48.13% | 1500000 | 18534.7826
SYN3900 spec. | 40 | 1200000 | 3 | 271 | 0.6025 | 19677.0239 | 542 | OK | 397.9% | 14400000 | 31036.3636
SYN2900 spec. | 17 | 510000 | 3 | 105 | 1.4176 | 19677.0239 | 210 | OK | 111.6% | 6120000 | 13159.0909

## English 1
Cálculo de ablandador Aquathin | [6 empty] | 65 |  | 1m3 = | 35.31 cft
|  |  | 30 | days / month |  | required grains/day: | 2891997.7865 |  | 1cft = | 28.32 liter
Total flow / day | 312 | m3/día | 82421.9369 | gpd |  | amount of units: | 2 |  | 1gal. = | 3.79 liter
Peak flow / h | 21 | m3/h | 92.4605 | gpm |  | peak flow speed: | 350 | l/min. | 1m3 = | 264.17 gal.
hardness | 600 | ppm | 35.0877 | grains |  | flow velocity: | 1.7597 | m/s | 1grano = | 17.1 ppm
Fe + Mn | 0 | ppm | 0 | grains |  | recom. Pipe Ø: | 2 1/2 | " | 1psi = | 0.71mwc
required
| cuft of | grain cap. | regen. per | peak flow | regen. | kg. of salt | max. peak flow |  | % poten. | total grains | valve
Unit model: | resin | per tank | day / tank | gpm | /day/tank | req./month | possible gpm | use | growth | of system / day | setting
HFD-SYN150K | 5 | 150000 | 6 | 48 | 5.133 | 12572.988 | 96 | OK | 24.48% | 3600000 | 4014.2857
HFD-SYN240K | 8 | 240000 | 6 | 48 | 3.1911 | 12506.2288 | 96 | OK | 99.17% | 5760000 | 6457.1429
HFD-SYN300K | 10 | 300000 | 6 | 48 | 2.5484 | 12484.133 | 96 | OK | 149% | 7200000 | 8085.7143
SYN 25K | 0.83333 | 25000 | 6 | 24 | 34.7372 | 14181.0275 | 48 | No | -79.25% | 600000 | 593.1818
SYN 30K | 1 | 30000 | 6 | 24 | 28.5107 | 13966.9743 | 48 | No | -75.1% | 720000 | 722.7273
SYN 45K | 1.5 | 45000 | 6 | 24 | 18.5407 | 13624.2265 | 48 | No | -62.66% | 1080000 | 1111.3636
SYN 75K | 2.5 | 75000 | 6 | 24 | 10.9102 | 13361.9068 | 48 | No | -37.76% | 1800000 | 1888.6364
ASC 15K/F | 0.5 | 15000 | 1 | 17 | 96.3999 | 52646.0781 | 34 | No | -98.96% | 30000 | 319.5652
ASC 25K/F | 0.83333 | 25000 | 1 | 17 | 57.84 | 49418.7323 | 34 | No | -98.27% | 50000 | 567.3913
ASC 40K/F | 1.3333 | 40000 | 1 | 17 | 36.15 | 47771.4413 | 34 | No | -97.23% | 80000 | 939.1304
ASC 45K/F | 1.5 | 45000 | 1 | 17 | 32.1333 | 47478.3649 | 34 | No | -96.89% | 90000 | 1063.0435
ASC 60K/F | 2 | 60000 | 1 | 17 | 24.1 | 46902.8696 | 34 | No | -95.85% | 120000 | 1434.7826
Mini Sodialite2k | 0.053333 | 1600 | 1 | 5 | 0.0011065 | días | 10 | No | -99.89% | 3200
AS2850-150K | 5 | 150000 | 1 | 48 | 9.64 | 45901.3848 | 96 | No | -89.63% | 300000 | 3665.2174
AS2850-240K | 8 | 240000 | 1 | 48 | 6.025 | 45657.6607 | 96 | No | -83.4% | 480000 | 5895.6522
AS2850-300K | 10 | 300000 | 1 | 48 | 4.82 | 45576.9934 | 96 | No | -79.25% | 600000 | 7382.6087
AS2900-240K | 8 | 240000 | 1 | 84 | 6.025 | 45657.6607 | 168 | No | -83.4% | 480000 | 5895.6522
AS2900-300K | 10 | 300000 | 1 | 84 | 4.82 | 45576.9934 | 168 | No | -79.25% | 600000 | 7382.6087
AS2900-510K | 17 | 510000 | 1 | 84 | 2.8353 | 45444.7493 | 168 | No | -64.73% | 1020000 | 12586.9565
AS3900-300K | 10 | 300000 | 1 | 105 | 4.82 | 45576.9934 | 210 | No | -79.25% | 600000 | 7382.6087
AS3900-510K | 17 | 510000 | 1 | 105 | 2.8353 | 45444.7493 | 210 | No | -64.73% | 1020000 | 12586.9565
AS3900-750K | 25 | 750000 | 1 | 105 | 1.928 | 45384.5501 | 210 | No | -48.13% | 1500000 | 18534.7826
SYN3900 spec. | 40 | 1200000 | 3 | 271 | 0.6025 | 19677.0239 | 542 | OK | 397.9% | 14400000 | 31036.3636
SYN2900 spec. | 17 | 510000 | 3 | 105 | 1.4176 | 19677.0239 | 210 | OK | 111.6% | 6120000 | 13159.0909

## Hoja1
|  | 25000 | 30000 | 45000 | 75000
|  | SYN-25K | SYN-30K | SYN-45K | SYN-75K
11.6959 | 200 | 1806.5217 | 2178.2609 | 3293.4783 | 5523.913
13.1579 | 225 | 1600 | 1930.4348 | 2921.7391 | 4904.3478
14.6199 | 250 | 1434.7826 | 1732.1739 | 2624.3478 | 4408.6957
16.0819 | 275 | 1299.6047 | 1569.9605 | 2381.0277 | 4003.1621
17.5439 | 300 | 1186.9565 | 1434.7826 | 2178.2609 | 3665.2174
19.0058 | 325 | 1091.6388 | 1320.4013 | 2006.689 | 3379.2642
20.4678 | 350 | 1009.9379 | 1222.3602 | 1859.6273 | 3134.1615
21.9298 | 375 | 939.1304 | 1137.3913 | 1732.1739 | 2921.7391
23.3918 | 400 | 877.1739 | 1063.0435 | 1620.6522 | 2735.8696
24.8538 | 425 | 822.5064 | 997.4425 | 1522.2506 | 2571.867
26.3158 | 450 | 773.913 | 939.1304 | 1434.7826 | 2426.087
27.7778 | 475 | 730.4348 | 886.9565 | 1356.5217 | 2295.6522
29.2398 | 500 | 691.3043 | 840 | 1286.087 | 2178.2609
30.7018 | 525 | 655.9006 | 797.5155 | 1222.3602 | 2072.0497
32.1637 | 550 | 623.7154 | 758.8933 | 1164.4269 | 1975.4941
33.6257 | 575 | 594.3289 | 723.6295 | 1111.5312 | 1887.3346
35.0877 | 600 | 567.3913 | 691.3043 | 1063.0435 | 1806.5217
36.5497 | 625 | 542.6087 | 661.5652 | 1018.4348 | 1732.1739
38.0117 | 650 | 519.7324 | 634.1137 | 977.2575 | 1663.5452
39.4737 | 675 | 498.5507 | 608.6957 | 939.1304 | 1600
40.9357 | 700 | 478.882 | 585.0932 | 903.7267 | 1540.9938
42.3977 | 725 | 460.5697 | 563.1184 | 870.7646 | 1486.057
43.8596 | 750 | 443.4783 | 542.6087 | 840 | 1434.7826
45.3216 | 775 | 427.4895 | 523.4222 | 811.2202 | 1386.8163
46.7836 | 800 | 412.5 | 505.4348 | 784.2391 | 1341.8478
48.2456 | 825 | 398.419 | 488.5375 | 758.8933 | 1299.6047
49.7076 | 850 | 385.1662 | 472.6343 | 735.0384 | 1259.8465

## Hoja2
|  | t0 | t1 | t2 | t3 | t4 | t5 | t6 | t7 | t8 | t9
Cap. Requerida granos/día | 401000
cap. Cilindro | 75000
cilindro 1 |  | t0: 75000; t2: 75000; t4: 75000; t6: 75000; t8: 75000 | 75000
cilindro 2 |  | t1: 75000; t3: 75000; t5: 75000; t7: 75000; t9: 75000 |  | 75000
900000
consumo sal | 270 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5

## caudal máx.m3
caudales maximos en m3/dia
| granos / ppm | 100 | 200 | 300 | 400 | 500 | 600 | 700 | 800
HFD-SYN150K | 1800000 | 1165.1461 | 582.5731 | 388.382 | 291.2865 | 233.0292 | 194.191 | 166.4494 | 145.6433
HFD-SYN240K | 2880000 | 1864.2338 | 932.1169 | 621.4113 | 466.0584 | 372.8468 | 310.7056 | 266.3191 | 233.0292
HFD-SYN300K | 3600000 | 2330.2922 | 1165.1461 | 776.7641 | 582.5731 | 466.0584 | 388.382 | 332.8989 | 291.2865
SYN 25K | 300000 | 194.191 | 97.0955 | 64.7303 | 48.5478 | 38.8382 | 32.3652 | 27.7416 | 24.2739
SYN 30K | 360000 | 233.0292 | 116.5146 | 77.6764 | 58.2573 | 46.6058 | 38.8382 | 33.2899 | 29.1287
SYN 45K | 540000 | 349.5438 | 174.7719 | 116.5146 | 87.386 | 69.9088 | 58.2573 | 49.9348 | 43.693
SYN 75K | 900000 | 582.5731 | 291.2865 | 194.191 | 145.6433 | 116.5146 | 97.0955 | 83.2247 | 72.8216
ASC 15K/F | 15000 | 9.7096 | 4.8548 | 3.2365 | 2.4274 | 1.9419 | 1.6183 | 1.3871 | 1.2137
ASC 25K/F | 25000 | 16.1826 | 8.0913 | 5.3942 | 4.0456 | 3.2365 | 2.6971 | 2.3118 | 2.0228
ASC 40K/F | 40000 | 25.8921 | 12.9461 | 8.6307 | 6.473 | 5.1784 | 4.3154 | 3.6989 | 3.2365
ASC 45K/F | 45000 | 29.1287 | 14.5643 | 9.7096 | 7.2822 | 5.8257 | 4.8548 | 4.1612 | 3.6411
ASC 60K/F | 60000 | 38.8382 | 19.4191 | 12.9461 | 9.7096 | 7.7676 | 6.473 | 5.5483 | 4.8548
Mini Sodialite2k | 1600 | 1035.6854 | 517.8427 | 345.2285 | 258.9214 | 207.1371 | 172.6142 | 147.9551 | 129.4607
AS2850-150K | 150000 | 97.0955 | 48.5478 | 32.3652 | 24.2739 | 19.4191 | 16.1826 | 13.8708 | 12.1369
AS2850-240K | 240000 | 155.3528 | 77.6764 | 51.7843 | 38.8382 | 31.0706 | 25.8921 | 22.1933 | 19.4191
AS2850-300K | 300000 | 194.191 | 97.0955 | 64.7303 | 48.5478 | 38.8382 | 32.3652 | 27.7416 | 24.2739
AS2900-240K | 240000 | 155.3528 | 77.6764 | 51.7843 | 38.8382 | 31.0706 | 25.8921 | 22.1933 | 19.4191
AS2900-300K | 300000 | 194.191 | 97.0955 | 64.7303 | 48.5478 | 38.8382 | 32.3652 | 27.7416 | 24.2739
AS2900-510K | 510000 | 330.1247 | 165.0624 | 110.0416 | 82.5312 | 66.0249 | 55.0208 | 47.1607 | 41.2656
AS3900-300K | 300000 | 194.191 | 97.0955 | 64.7303 | 48.5478 | 38.8382 | 32.3652 | 27.7416 | 24.2739
AS3900-510K | 510000 | 330.1247 | 165.0624 | 110.0416 | 82.5312 | 66.0249 | 55.0208 | 47.1607 | 41.2656
AS3900-750K | 750000 | 485.4776 | 242.7388 | 161.8259 | 121.3694 | 97.0955 | 80.9129 | 69.3539 | 60.6847
SYN3900 spec. | 7200000 | 4660.5845 | 2330.2922 | 1553.5282 | 1165.1461 | 932.1169 | 776.7641 | 665.7978 | 582.5731

## caudal máx. l-s
caudales maximos en l/seg
| granos / ppm | 100 | 200 | 300 | 400 | 500 | 600 | 700 | 800
HFD-SYN150K | 1800000 | 13.4855 | 6.7427 | 4.4952 | 3.3714 | 2.6971 | 2.2476 | 1.9265 | 1.6857
HFD-SYN240K | 2880000 | 21.5768 | 10.7884 | 7.1923 | 5.3942 | 4.3154 | 3.5961 | 3.0824 | 2.6971
HFD-SYN300K | 3600000 | 26.971 | 13.4855 | 8.9903 | 6.7427 | 5.3942 | 4.4952 | 3.853 | 3.3714
SYN 25K | 300000 | 2.2476 | 1.1238 | 0.74919 | 0.5619 | 0.44952 | 0.3746 | 0.32108 | 0.28095
SYN 30K | 360000 | 2.6971 | 1.3485 | 0.89903 | 0.67427 | 0.53942 | 0.44952 | 0.3853 | 0.33714
SYN 45K | 540000 | 4.0456 | 2.0228 | 1.3485 | 1.0114 | 0.80913 | 0.67427 | 0.57795 | 0.50571
SYN 75K | 900000 | 6.7427 | 3.3714 | 2.2476 | 1.6857 | 1.3485 | 1.1238 | 0.96325 | 0.84284
ASC 15K/F | 15000 | 0.11238 | 0.05619 | 0.03746 | 0.028095 | 0.022476 | 0.01873 | 0.016054 | 0.014047
ASC 25K/F | 25000 | 0.1873 | 0.093649 | 0.062433 | 0.046825 | 0.03746 | 0.031216 | 0.026757 | 0.023412
ASC 40K/F | 40000 | 0.29968 | 0.14984 | 0.099892 | 0.074919 | 0.059936 | 0.049946 | 0.042811 | 0.03746
ASC 45K/F | 45000 | 0.33714 | 0.16857 | 0.11238 | 0.084284 | 0.067427 | 0.05619 | 0.048162 | 0.042142
ASC 60K/F | 60000 | 0.44952 | 0.22476 | 0.14984 | 0.11238 | 0.089903 | 0.074919 | 0.064217 | 0.05619
Mini Sodialite2k | 1600 | 0.011987 | 0.0059936 | 0.0039957 | 0.0029968 | 0.0023974 | 0.0019978 | 0.0017124 | 0.0014984
AS2850-150K | 150000 | 1.1238 | 0.5619 | 0.3746 | 0.28095 | 0.22476 | 0.1873 | 0.16054 | 0.14047
AS2850-240K | 240000 | 1.7981 | 0.89903 | 0.59935 | 0.44952 | 0.35961 | 0.29968 | 0.25687 | 0.22476
AS2850-300K | 300000 | 2.2476 | 1.1238 | 0.74919 | 0.5619 | 0.44952 | 0.3746 | 0.32108 | 0.28095
AS2900-240K | 240000 | 1.7981 | 0.89903 | 0.59935 | 0.44952 | 0.35961 | 0.29968 | 0.25687 | 0.22476
AS2900-300K | 300000 | 2.2476 | 1.1238 | 0.74919 | 0.5619 | 0.44952 | 0.3746 | 0.32108 | 0.28095
AS2900-510K | 510000 | 3.8209 | 1.9104 | 1.2736 | 0.95522 | 0.76418 | 0.63681 | 0.54584 | 0.47761
AS3900-300K | 300000 | 2.2476 | 1.1238 | 0.74919 | 0.5619 | 0.44952 | 0.3746 | 0.32108 | 0.28095
AS3900-510K | 510000 | 3.8209 | 1.9104 | 1.2736 | 0.95522 | 0.76418 | 0.63681 | 0.54584 | 0.47761
AS3900-750K | 750000 | 5.619 | 2.8095 | 1.873 | 1.4047 | 1.1238 | 0.93649 | 0.80271 | 0.70237
SYN3900 spec. | 7200000 | 53.9419 | 26.971 | 17.9807 | 13.4855 | 10.7884 | 8.9903 | 7.706 | 6.7427

## Vol de resina vs tamaño
Calc. Volumen de resina cartridge
granos | litros resina | 100 | 200 | 300 | 400 | 500 | 600 | 700 | 800
500 | 0.472 | 323.6517 | 161.8259 | 107.8839 | 80.9129 | 64.7303 | 53.9419 | 46.236 | 40.4565
1000 | 0.944 | 647.3034 | 323.6517 | 215.7678 | 161.8259 | 129.4607 | 107.8839 | 92.4719 | 80.9129
1500 | 1.416 | 970.9551 | 485.4776 | 323.6517 | 242.7388 | 194.191 | 161.8259 | 138.7079 | 121.3694
2000 | 1.888 | 1294.6068 | 647.3034 | 431.5356 | 323.6517 | 258.9214 | 215.7678 | 184.9438 | 161.8259
2500 | 2.36 | 1618.2585 | 809.1292 | 539.4195 | 404.5646 | 323.6517 | 269.7097 | 231.1798 | 202.2823
3000 | 2.832 | 1941.9102 | 970.9551 | 647.3034 | 485.4776 | 388.382 | 323.6517 | 277.4157 | 242.7388
3500 | 3.304 | 2265.5619 | 1132.781 | 755.1873 | 566.3905 | 453.1124 | 377.5937 | 323.6517 | 283.1952
4000 | 3.776 | 2589.2136 | 1294.6068 | 863.0712 | 647.3034 | 517.8427 | 431.5356 | 369.8877 | 323.6517
4500 | 4.248 | 2912.8653 | 1456.4326 | 970.9551 | 728.2163 | 582.5731 | 485.4776 | 416.1236 | 364.1082
5000 | 4.72 | 3236.517 | 1618.2585 | 1078.839 | 809.1292 | 647.3034 | 539.4195 | 462.3596 | 404.5646
1m3 = | 35.31 cft
1cft = | 28.32 litro

## calc. volumen estanque
| litros / hora | lit./min. | Volúmen total utilizable: | 402.0333 | litros
caudal de entrada | 62 | 1.0333 | durante | 31 | minutos
caudal peak de salida | 800 | 13.3333 | tiempo de rellenado | 358.0645 | minutos
volúmen estanque | 370 |  |  | 5 | horas
|  |  |  | 58.0645 | minutos
Minuto | litros
0 | 370
1 | 357.7
2 | 345.4
3 | 333.1
4 | 320.8
5 | 308.5
6 | 296.2
7 | 283.9
8 | 271.6
9 | 259.3
10 | 247
11 | 234.7
12 | 222.4
13 | 210.1
14 | 197.8
15 | 185.5
16 | 173.2
17 | 160.9
18 | 148.6
19 | 136.3
20 | 124
21 | 111.7
22 | 99.4
23 | 87.1
24 | 74.8
25 | 62.5
26 | 50.2
27 | 37.9
28 | 25.6
29 | 13.3
30 | 1
31 | -11.3
32 | -23.6
33 | -35.9
34 | -48.2
35 | -60.5
36 | -72.8
37 | -85.1
38 | -97.4
39 | -109.7
40 | -122
41 | -134.3
42 | -146.6
43 | -158.9
44 | -171.2
45 | -183.5
46 | -195.8
47 | -208.1
48 | -220.4
49 | -232.7
50 | -245
51 | -257.3
52 | -269.6
53 | -281.9
54 | -294.2
55 | -306.5
56 | -318.8
57 | -331.1
58 | -343.4
59 | -355.7
60 | -368
61 | -380.3
62 | -392.6
63 | -404.9
64 | -417.2
65 | -429.5
66 | -441.8
67 | -454.1
68 | -466.4
69 | -478.7
70 | -491
71 | -503.3
72 | -515.6
73 | -527.9
74 | -540.2
75 | -552.5
76 | -564.8
77 | -577.1
78 | -589.4
79 | -601.7
80 | -614